## Decision tool
Decision tool for reducing airborne transmission risk in the UK care home context
Notes:
1 | This tool has been created to allow decisions to be made on minimum air ventilation rates for communal rooms in the care home context.
2 | It takes into account occupancy time, social distancing, well accepted minimum ventilation rates based on indoor air quality, and maximum occupant numbers.
3 | It has been made using the Airborne Infection Risk Calculator (AIRC) modelling tool v2.1 (https://research.qut.edu.au/ilaqh/projects/expiratory-aerosols-and-infection-spread), assuming an activity level light activity and oral breathing, and a time corresponding to a risk of approximately 0.5%.
4 | You can either use the top three tables manually to make decisions based on room volume, occupancy numbers and occupancy time, in order to determine an air change rate per hour, in order to find what that equates to in m3/h. A worked example is given in the care homes strategy document (section 21).
5 | Alternatively, enter relevant data in the yellow boxes below to determine how much ventilation and/or filtration is required in your particular context.
6 | In general, the principle should be to try to install ventilation first before considering HEPA filters, because other indoor air quality parameters (e.g. CO2) is addressed by the first but not the second method.
Step
1 | Measure the room dimension (communal rooms)
| Width (m) | Length (m) | Height (m) | Volume (m3)
| 8 | 8 | 2.4 | 153.6
2 | Enter data on time and occupancy in order to get air changes per hour required - this should be based on the worst case scenario (e.g. Christmas Eve)
| 11 | Maximum number of occupants (residents and staff) to maintain social distance (6 m2/person)
| 3 | Select the maximum time, in hours, that people would continuously remain in that room
| 5 | Enter the number of occupants (residents and staff) that would be in that room at any one time
| 2.5 | Air changes per hour needed as a minimum
3 | Decide how to achieve that using ventilation and/or filtration equipment available:
| 384 | Total flow rate required (in m3/h)
| 100 | Ventilation unit flow rate (in m3/h) of the unit you intend to buy (if going for a single room ventilation unit, see separate tab for options)
| 1 | Number of Mechanical Ventilation with Heat Recovery (MVHR) units that are planned
| 284 | Remaining flow rate (in m3/h) that will need to be provided additionally from a HEPA room filter (see HEPA filter tab for options)
|  | Air Changes per Hour | [9 empty] | Air Changes per Hour | [9 empty] | Air Changes per Hour
|  | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 |  |  | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 |  |  | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
Room Volume (m3) | 50 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | Room Volume (m3) | 50 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | Room Volume (m3) | 50 | 25 | 50 | 75 | 100 | 125 | 150 | 175 | 200
| 100 | 1 | 1.5 | 1.5 | 2 | 2 | 2.5 | 2.5 | 3 |  | 100 | 2 | 4 | 6 | 7 | 7 | 7 | 7 | 7 |  | 100 | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400
| 150 | 1.5 | 2 | 2.5 | 2.5 | 3 | 3.5 | 3.5 | 4 |  | 150 | 3 | 6 | 9 | 10 | 10 | 10 | 10 | 10 |  | 150 | 75 | 150 | 225 | 300 | 375 | 450 | 525 | 600
| 200 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 |  | 200 | 4 | 8 | 12 | 14 | 14 | 14 | 14 | 14 |  | 200 | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800
| 250 | 2.5 | 3 | 3.5 | 4 | 5 | 5.5 | 6 | 7 |  | 250 | 5 | 10 | 15 | 17 | 17 | 17 | 17 | 17 |  | 250 | 125 | 250 | 375 | 500 | 625 | 750 | 875 | 1000
| 300 | 3 | 3.5 | 4 | 5 | 6 | 6.5 | 7.5 | 8 |  | 300 | 6 | 12 | 18 | 21 | 21 | 21 | 21 | 21 |  | 300 | 150 | 300 | 450 | 600 | 750 | 900 | 1050 | 1200
| 350 | 3 | 4 | 5 | 6 | 7 | 7.5 | 8.5 | 9.5 |  | 350 | 7 | 14 | 21 | 24 | 24 | 24 | 24 | 24 |  | 350 | 175 | 350 | 525 | 700 | 875 | 1050 | 1225 | 1400
| 400 | 3.5 | 4.5 | 5.5 | 6.5 | 7.5 | 9 | 10 | 11 |  | 400 | 8 | 16 | 24 | 28 | 28 | 28 | 28 | 28 |  | 400 | 200 | 400 | 600 | 800 | 1000 | 1200 | 1400 | 1600
|  | Maximum Time of Occupancy (h) | [9 empty] | Maximum Occupants | [9 empty] | Total Flowrate (m3/h)
|  | Air Changes per Hour | [9 empty] | Air Changes per Hour
|  | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 |  |  | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
Room Volume (m3) | 50 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Room Volume (m3) | 50 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| 100 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 100 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16
| 150 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 150 | 3 | 6 | 9 | 12 | 15 | 18 | 21 | 24
| 200 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 200 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32
| 250 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 250 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
| 300 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 300 | 6 | 12 | 18 | 24 | 30 | 36 | 42 | 48
| 350 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 350 | 7 | 14 | 21 | 28 | 35 | 42 | 49 | 56
| 400 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 400 | 8 | 16 | 24 | 32 | 40 | 48 | 56 | 64
|  | 6 m2/person Occupancy | [9 empty] | 25 m3/h/person Occupancy ~ 1,000 ppm CO2

## Single room ventilation options
Single room ventilation units with heat recovery - options
Notes:
1 | This analysis has been carried out by Ecospheric, a Manchester-based company specialising in Passivhaus new build and retrofit (www.ecospheric.co.uk)
2 | Larger whole building Mechanical Ventilation with Heat Recovery (MVHR) is the ideal longer term solution (they are not listed here, there are enough on the market). However, single room ventilation units can also provide an interim solution for adequately ventilating communal rooms.
3 | Advantages of using single room MVHR units is that cost can be less, installation can be quicker and easier, and they can save space. Disadvantages are limited flow rates and limited number of suitable options.
4 | Below we have listed out various technical options, showing flow rate, price and other information. The flow rate (columns G & H) is what you need to enter in the decision tool.
5 | While we have listed a variety, we recommend going with those showin in green or orange (orange can have some supply issues). You should always choose a unit with 2 fans as a minimum to provide balanced pressure and avoid draughts.
6 | For those units that have flow rate controlled by CO2, humidity or temperature, ensure these can be overriden so that flow rate can be maintained.
| Manufacturer | Model | Supplier | Heat Recovery Efficiency | Electric efficiency | Application range |  | Noise | Price per unit | Links | Maintenance info | Number of fans | Recommended? Benefits/issues | Other comments | Contact
|  |  |  | % | Wh/m³ | m³/h | m³/h | dB(A) | £ or €
Recommended | Vaventis | Fresh-r | https://shop.fresh-r.eu/ | 78 | 0.2 - 0.4 | 25 | 120 | 35 = 25 65 = 30 80 = 35 120 = 45 | 2,250 Euro ex VAT | PassivHaus component award winner Technical datasheet | Rinse heat exchanger every 6 months if no filters. Clean upper and lower duct pipe every 2 years. | 2 | The best technical solution, most expensive also. Would require filters adding to the base cost as does not come as standard. Very slim and can be completely recessed in some wall situations. Copper heat exchanger offers excellent hygiene properties and also removes the risk of it freezing in sub-zero conditions. Best range for air exchange rates may result in less devices being necessary in most situations. | Demand-controlled according to CO2, humidty & temperature. Cascade based system and can have ducts attached if needed wifi connected. Filters as options. | https://shop.fresh-r.eu/contactus
| bluMartin | FreeAir | Paul Heat Recovery Scotland https://www.paulheatrecovery.co.uk | 87 | 0.24 | 8 | 100 | 20m3/hr = 17 50 = 34 70 = 48 100 = 51 | £1,652 - 2,074 inc VAT | https://www.paulheatrecovery.co.uk/cascade-mvhr/ https://www.paulheatrecovery.co.uk/wp-content/uploads/2017/03/BluMartin-Brochure-2017.pdf | https://www.paulheatrecovery.co.uk/cascade-mvhr/filter-change-for-the-freeair-100/ Annual replacement of filters | 2 | Good price and performance. Needs a large wall void to accommodate making it more difficult to accommodate in retrofit scenarios. As it comes fully equiped with sensors, wifi and filters at the best price point, this would be the device to specify if it wasn't for the depth of the device. | Demand-controlled according to CO2, humidty & temperature. Cascade based system and can have two ducts attached if needed. Passivhaus certified component. Wifi connection. | Stefan Huber
| Zehnder | Comfoair 70 | No UK or Ireland supplier | 85 | 0.24 | 15 | 60 | 34-47 | 1,600 Euro list price | https://www.international.zehnder-systems.com/products-and-systems/comfosystems/zehnder-comfoair-70 https://www.international.zehnder-systems.com/download/9796/61694/Zehnder_ComfoAir_70_TES_SI_en.pdf | Clean filters | 2 | Compact neat device with the best performance ratio of all SRHRVs, but no supply outlet in the UK. Would need to contact and negotiate with Zehnder directly. CO2 and humidty sensors are not standard and so would increase price. | Optional control by CO2 and humidity sensor. | Jason.Bennett@zehnder.co.uk
Caution | Blauberg | Freshbox | https://www.blauberg.co.uk/en/blauberg-freshbox-single-room-heat-recovery-ventilation-wall-fan-unit-supply-extract-air-wifi | 92 | 0.53 | 0 | 100 | max 47 | £1,300 inc VAT | https://www.blauberg.co.uk/en/amfilerating/file/download/file_id/212/ | Clean filters | 2 | Not a Passivhaus certified solution, will require pre-heater. | Optional post heater. Optional CO2 and humidity sensor. Wifi connection. | Tel: 0116 216 0650 E-mail: jackie.goggans@blauberg.co.uk
| Dimplex | DL50 WH2 | https://www.conrad.com/p/dimplex-dl-50-wh2-air-distribution-system-230-v-45-mh-2144269 | 83 | 0.31 | 15 | 45 | max 51 | 1,629 Euro inc VAT | http://www.dimplex.de/fileadmin/dimplex/downloads/datenblatt/en/800-37477_P-1-1007V3-EN_Factsheet_DL50W2_web2.pdf | Clean filters | 2 | Essentially this is a similar device to the Comfoair 70, slightly worse in pretty much everyway apart from app control. Likely suffers from similar supply issues. | Remote control with potential smartphone app (via Somfy interface).
| Meltem Wärmerückgewinnung | M-WRG-II P | No UK supplier | 82 | 0.35 | 10 | 77 | max 46 | 1,131 Euro | https://database.passivehouse.com/Media/certified_components_v2/certificate/pdf/2020_zd_meltem_m-wrg-II_p_en.pdf https://www.meltem.com/en/ | Clean filters | 2 | Very suitable device but UK supply issues.
| Blauberg | Vento Expert Duo-air | https://www.blauberg.co.uk/en/blauberg-duo-air-continuous-decentralised-d-mvhr-heat-recovery-energy-recovery-unit-with-smart-wifi-control | up to 85 | 0.22 | 0 | 30 | max 51 | £561 inc VAT | https://www.blauberg.co.uk/en/amfilerating/file/download/file_id/652/ | Clean filters | 2 | Not capable of achieving air flow necessary for a kitchen. Very noisy given it will have to operate at max speed to achieve desired flow rates. Higher chance of short circuiting (i.e. extracted air coming back in via the inlet). Only suitable for one room, but can be combined with others and linked via wifi. | Ceramic heat retaining exhanger. One fan extracts and the other supplies. They swap every 70 seconds. | Tel: 0116 216 0650 E-mail: jackie.goggans@blauberg.co.uk
Not recommended | Zehnder | Comfospot 50 | No UK or Ireland supplier | 85 | 0.3 | 15 | 50 | max 41 | 1,076 Euro inc vat list price | https://www.international.zehnder-systems.com/products-and-systems/comfosystems/zehnder-comfospot-50 | Clean filters | 2 | Flow rate too low and no UK supplier makes this an unlikely selection. Would need to contact and negotiate with Zehnder directly. CO2 and humidty sensors are not standard and so would increase price. | Optional control by humidty and CO2 sensors. Can also work in enthalpy mode and recover humidity.
| Blauberg | Vento Expert Maxi air | https://www.blauberg.co.uk/en/blauberg-maxi-air-smart-wifi-heat-recovery-unit-decentralised-single-room-ventilator-wall-mounted | up to 87 | 0.16 | 0 | 108 | max 50 | £460 inc VAT | https://www.blauberg.co.uk/en/amfilerating/file/download/file_id/673/ | Clean filters | 2 * |  | Ceramic heat retaining exhanger. In or out not both simultaneousy. | Tel: 0116 216 0650 E-mail: jackie.goggans@blauberg.co.uk
| Xpelair | Muro Heat Recovery | https://www.xpelair.co.uk/product/xhrm-muro-heat-recovery-unit | 83 |  |  |  | max 39 | 1069 |  |  | 2
| envirovent | HeatSava | https://www.envirovent.com/products/heat-recovery-ventilation-mvhr/heatsava/ | 75 | 0.25 - 0.5 | 0 | 47 | max 41 | 341 | Product Page Technical Datasheet | No info | 2 |  | Ventilation rate varies with humidity. No wifi connection. Wireless manual controller. Auto summer bypass. | 0345 2727810
| Ventaxia | Lo-Carbon Tempra /SELV | https://www.vent-axia.com/range/lo-carbon-tempraselv | 78 |  |  | 54 |  | £200 - 400 ex VAT |  | Clean filters | 1
| Sud wind | Ambientka Solo | https://www.suedwind.it/en?gclid=CjwKCAjwte71BRBCEiwAU_V9h6peYL4DAU2VjavbWB4mnzE_9DTmYUhH9Q7n2DYvuJobHs9WsWt1ghoCTOcQAvD_BwE | up to 93% |  | 0 | 60 | 18 - 42 | 279 Euro inc VAT |  | Clean filters | 1 |  | Humidistat and optional C02 sensor. Optional WIFI.
| Vents | Twin fresh | https://ventilation-system.com/series/twinfresh-standard | 90 |  |  |  | 14 - 41 |  |  | Clean filters | 1 |  | Ceramic heat retaining exhanger. In or out not both simultaneousy.
| Vents | Micra | https://ventilation-system.com/series/micra-60 | up to 79% | 0.25 | 0 | 60 | max 29 | ~£450 inc VAT |  | Clean filters | 2
| Mitsubishi | VL-100(E)U5-E | http://library.mitsubishielectric.co.uk/pdf/book/VL-100-EU5-E_Product_Information_Sheet#page-1-2 | Up to 79% | 0.32 | 61 | 106 | 27 - 38 |  |  |  | 1

## Portable HEPA options
Example Portable HEPA Filter Options
List obtained from HARVARD - CU BOULDER PORTABLE AIR CLEANER CALCULATOR FOR SCHOOLS v1.2 (Allen, Cedeno-Laurent, Miller)
https://tinyurl.com/portableaircleanertool
Portable Air Cleaners | Clean Air Delivery Rate (m3/h)
Honeywell HEPA Air Purifier HPA100 | 169.8
Blueair Classic 205 | 339.6
Honeywell HEPA Air Purifier HPA200 | 339.6
Coway AP-1512HH | 417.708
Blueair PRO M | 483.93
Honeywell HEPA Air Purifier HPA300 | 509.4
LivePure Bali Multi-Room | 551.85
Whirlpool WPPRO 20000 | 556.944
QuietPure Home | 579.018
Winix 5500-2 Air Cleaner | 594.3
Honeywell PowerPlus HEPA Air Puriifer HPA3300B | 602.79
Levoit LV-H135 | 611.28
Coway AirMega 400 | 706.368
Blueair Classic 605 | 849
Medify | 950.88
Blueair PRO L | 1069.74

## Data
Volume (m3) | ACH | 1% | 0.1% |  | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 0.5
50 | 0.5 | 75 | 19 | 50 | 19 | 20 | 20 | 21 | 22 | 22 | 23 | 24 | 1
50 | 1 | 84 | 20 | 100 | 28 | 30 | 31 | 32 | 34 | 36 | 37 | 39 | 1.5
50 | 1.5 | 93 | 20 | 150 | 36 | 38 | 40 | 42 | 45 | 48 | 51 | 54 | 2
50 | 2 | 104 | 21 | 200 | 43 | 45 | 48 | 52 | 55 | 59 | 64 | 68 | 2.5
50 | 2.5 | 116 | 22 | 250 | 49 | 52 | 56 | 61 | 66 | 71 | 76 | 82 | 3
50 | 3 | 128 | 22 | 300 | 54 | 59 | 64 | 69 | 76 | 82 | 89 | 97 | 3.5
50 | 3.5 | 141 | 23 | 350 | 60 | 65 | 71 | 78 | 85 | 93 | 102 | 111 | 4
50 | 4 | 154 | 24 | 400 | 65 | 71 | 79 | 87 | 95 | 105 | 115 | 125 | 4.5
100 | 0.5 | 120 | 28 | [9 empty] | 5
100 | 1 | 140 | 30 |  | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5.5
100 | 1.5 | 163 | 31 | 50 | 75 | 84 | 93 | 104 | 116 | 128 | 141 | 154 | 6
100 | 2 | 188 | 32 | 100 | 120 | 140 | 163 | 188 | 214 | 241 | 269 | 297 | 6.5
100 | 2.5 | 214 | 34 | 150 | 162 | 195 | 233 | 272 | 313 | 355 | 397 | 439 | 7
100 | 3 | 241 | 36 | 200 | 203 | 250 | 302 | 356 | 412 | 468 | 540 | 600 | 7.5
100 | 3.5 | 269 | 37 | 250 | 243 | 305 | 372 | 440 | 522 | 594 | 672 | 744 | 8
100 | 4 | 297 | 39 | 300 | 284 | 360 | 441 | 540 | 624 | 714 | 798 | 888 | 8.5
150 | 0.5 | 162 | 36 | 350 | 324 | 415 | 522 | 624 | 726 | 828 | 930 | 1032 | 9
150 | 1 | 195 | 38 | 400 | 364 | 469 | 594 | 708 | 828 | 948 | 1062 | 1188 | 9.5
150 | 1.5 | 233 | 40 | [9 empty] | 10
150 | 2 | 272 | 42 |  | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 10.5
150 | 2.5 | 313 | 45 | 50 | 0.78333 | 0.86667 | 0.94167 | 1.0417 | 1.15 | 1.25 | 1.3667 | 1.4833 | 11
150 | 3 | 355 | 48 | 100 | 1.2333 | 1.4167 | 1.6167 | 1.8333 | 2.0667 | 2.3083 | 2.55 | 2.8
150 | 3.5 | 397 | 51 | 150 | 1.65 | 1.9417 | 2.275 | 2.6167 | 2.9833 | 3.3583 | 3.7333 | 4.1083
150 | 4 | 439 | 54 | 200 | 2.05 | 2.4583 | 2.9167 | 3.4 | 3.8917 | 4.3917 | 5.0333 | 5.5667
200 | 0.5 | 203 | 43 | 250 | 2.4333 | 2.975 | 3.5667 | 4.175 | 4.9 | 5.5417 | 6.2333 | 6.8833
200 | 1 | 250 | 45 | 300 | 2.8167 | 3.4917 | 4.2083 | 5.075 | 5.8333 | 6.6333 | 7.3917 | 8.2083
200 | 1.5 | 302 | 48 | 350 | 3.2 | 4 | 4.9417 | 5.85 | 6.7583 | 7.675 | 8.6 | 9.525
200 | 2 | 356 | 52 | 400 | 3.575 | 4.5 | 5.6083 | 6.625 | 7.6917 | 8.775 | 9.8083 | 10.9417 | Volume | Time
200 | 2.5 | 412 | 55 | [9 empty] | 150 | 3 |  | 5 | 2.5
200 | 3 | 468 | 59 |  | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | index | hours | ACH | 25 m3/h/p | Max ACH
200 | 3.5 | 480 | 64 | 50 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 2 | 1.5 | 0.5 | 1 | 1
200 | 4 | 480 | 68 | 100 | 1 | 1.5 | 1.5 | 2 | 2 | 2.5 | 2.5 | 3 | 3 | 2 | 1 | 1 | 1
250 | 0.5 | 243 | 49 | 150 | 1.5 | 2 | 2.5 | 2.5 | 3 | 3.5 | 3.5 | 4 | 4 | 2.5 | 1.5 | 1 | 1.5
250 | 1 | 305 | 52 | 200 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 5 | 2.5 | 2 | 1 | 2
250 | 1.5 | 372 | 56 | 250 | 2.5 | 3 | 3.5 | 4 | 5 | 5.5 | 6 | 7 | 6 | 3 | 2.5 | 1 | 2.5
250 | 2 | 440 | 61 | 300 | 3 | 3.5 | 4 | 5 | 6 | 6.5 | 7.5 | 8 | 7 | 3.5 | 3 | 1 | 3
250 | 2.5 | 480 | 66 | 350 | 3 | 4 | 5 | 6 | 7 | 7.5 | 8.5 | 9.5 | 8 | 3.5 | 3.5 | 1 | 3.5
250 | 3 | 480 | 71 | 400 | 3.5 | 4.5 | 5.5 | 6.5 | 7.5 | 9 | 10 | 11 | 9 | 4 | 4 | 1 | 4
250 | 3.5 | 480 | 76
250 | 4 | 480 | 82
300 | 0.5 | 284 | 54
300 | 1 | 360 | 59
300 | 1.5 | 441 | 64
300 | 2 | 480 | 69
300 | 2.5 | 480 | 76
300 | 3 | 480 | 82
300 | 3.5 | 480 | 89
300 | 4 | 480 | 97
350 | 0.5 | 324 | 60
350 | 1 | 415 | 65
350 | 1.5 | 480 | 71
350 | 2 | 480 | 78
350 | 2.5 | 480 | 85
350 | 3 | 480 | 93
350 | 3.5 | 480 | 102
350 | 4 | 480 | 111
400 | 0.5 | 364 | 65
400 | 1 | 469 | 71
400 | 1.5 | 480 | 79
400 | 2 | 480 | 87
400 | 2.5 | 480 | 95
400 | 3 | 480 | 105
400 | 3.5 | 480 | 115
400 | 4 | 480 | 125